## Cover
ALINVEST |  | Plant Cable Length MTO
Cover
CUSTOMER: |  | ALINVEST | PREPARED: | RORI
PROJECT CODE: |  | 2558 | REVIEWED: | ANSA
PROJECT NAME: |  | E2558 ALINVEST | APPROVED: | ANSA
DOCUMENT CODE: |  | 2558-0000-GEN-E-MTO-CBLS-A Plant Cable Length MTO | REVISION: | A
DATE: |  | 2025-12-09 | PAGE: | 1 of 3
Revision Control
REV | DATE | DESCRIPTON |  | PAGE
A | 2025-12-09 | Initial revision |  | 1,2,3
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## Table of Contents
ALINVEST |  | Plant Cable Length MTO
Table of Contents
CUSTOMER: |  | ALINVEST | PREPARED: | JOAN
PROJECT CODE: |  | 2558 | REVIEWED: | ANSA
PROJECT NAME: |  | E2558 ALINVEST | APPROVED: | ANSA
DOCUMENT CODE: |  | 2558-0000-GEN-E-MTO-CBLS-A Plant Cable Length MTO | REVISION: | A
DATE: |  | 2025-12-09 | PAGE: | 2 of 3
Table of contents
SEC | DESCRIPTON |  |  | PAGE
0 | Power and control cables |  |  | 3
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
The drawing(s), document(s) and the information contained herein are the property of INDUSTRIAL FURNACES INSERTEC. And they shall not be disclosed, reproduced or used in any manner without the prior written consent of INDUSTRIAL FURNACES INSERTEC. Offenders will be held liable for the payment of damages.

## PLANT CABLE MTO
ALINVEST |  | Plant Cable Length MTO
Cable Length MTO
CUSTOMER: |  | ALINVEST |  |  |  |  | PREPARED: | RORI
PROJECT CODE: |  | 2558 |  |  |  |  | REVIEWED: | ANSA
PROJECT NAME: |  | E2558 ALINVEST |  |  |  |  | APPROVED: | ANSA
DOCUMENT CODE: |  | 2558-0000-GEN-E-MTO-CBLS-A Plant Cable Length MTO |  |  |  |  | REVISION: | A
DATE: |  | 2025-12-09 |  |  |  |  | PAGE: | 3 of 3
Item | Type | Cable Reference | Category | Unit | Quantity | Quantity | Remarks |  | Jednotková cena v Kč bez DPH | Celková cena v Kč bez DPH | Požadavky na doplnění specifikace | Vysvětlení Zadavatele
1 | 4G70 | RV-K 0,6/1kV | CWP01 | METERS | 3104 | 3726 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | For all cases no less than 2,5 mm2(≤14 AWG) will be used. Application For DOL/RDOL starting types, electrical panels supply, etc. Conductor material Copper Isolation XLPE Composition Insulated conductors laid up together. Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Minimun curvature radius 200mm Shield No Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
2 | 4G35 | V-K 0,6/1kV | CWP01 | METERS | 80 | 96 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | For all cases no less than 2,5 mm2(≤14 AWG) will be used. Application For DOL/RDOL starting types, electrical panels supply, etc. Conductor material Copper Isolation XLPE Composition Insulated conductors laid up together. Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Minimun curvature radius 200mm Shield No Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
3 | 4G35+SH | RC4V-K 0,6/1kV | CWP02 | METERS | 521 | 626 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | Application For VFD commanded motor starting types, Thyristor groups fed heaters, etc. Conductor material Copper Isolation XLPE Composition Up to 10mm2: Insulated conductors laid up together. From 16mm2: 3x + 3G configuration, the protection core Yellow/Green is divided in three cores Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Shield Aluminium/polyester tape + Tinned copper wire braid (80%) Total coverage:100% Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
4 | 4G25 | RV-K 0,6/1kV | CWP01 | METERS | 647 | 778 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | For all cases no less than 2,5 mm2(≤14 AWG) will be used. Application For DOL/RDOL starting types, electrical panels supply, etc. Conductor material Copper Isolation XLPE Composition Insulated conductors laid up together. Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Minimun curvature radius 200mm Shield No Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
5 | 4G16 | RV-K 0,6/1kV | CWP01 | METERS | 459 | 552 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | For all cases no less than 2,5 mm2 (≤14 AWG) will be used. Application For DOL/RDOL starting types, electrical panels supply, etc. Conductor material Copper Isolation XLPE Composition Insulated conductors laid up together. Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Minimun curvature radius 200mm Shield No Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
6 | 4G16+SH | RC4V-K 0,6/1kV | CWP02 | METERS | 499 | 600 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | Application For VFD commanded motor starting types, Thyristor groups fed heaters, etc. Conductor material Copper Isolation XLPE Composition Up to 10mm2: Insulated conductors laid up together. From 16mm2: 3x + 3G configuration, the protection core Yellow/Green is divided in three cores Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Shield Aluminium/polyester tape + Tinned copper wire braid (80%) Total coverage:100% Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
7 | 4G10+SH | RC4V-K 0,6/1kV | CWP02 | METERS | 1342 | 1612 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | Application For VFD commanded motor starting types, Thyristor groups fed heaters, etc. Conductor material Copper Isolation XLPE Composition Up to 10mm2: Insulated conductors laid up together. From 16mm2: 3x + 3G configuration, the protection core Yellow/Green is divided in three cores Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Shield Aluminium/polyester tape + Tinned copper wire braid (80%) Total coverage:100% Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
8 | 4G6 | RV-K 0,6/1kV | CWP01 | METERS | 1052 | 1264 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | For all cases no less than 2,5 mm2 (≤14 AWG) will be used. Application For DOL/RDOL starting types, electrical panels supply, etc. Conductor material Copper Isolation XLPE Composition Insulated conductors laid up together. Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Minimun curvature radius 200mm Shield No Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
9 | 4G4 | RV-K 0,6/1kV | CWP01 | METERS | 200 | 240 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | For all cases no less than 2,5 mm2 (≤14 AWG) will be used. Application For DOL/RDOL starting types, electrical panels supply, etc. Conductor material Copper Isolation XLPE Composition Insulated conductors laid up together. Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Minimun curvature radius 200mm Shield No Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
10 | 4G4+SH | RC4V-K 0,6/1kV | CWP02 | METERS | 500 | 600 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | Application For VFD commanded motor starting types, Thyristor groups fed heaters, etc. Conductor material Copper Isolation XLPE Composition Up to 10mm2: Insulated conductors laid up together. From 16mm2: 3x + 3G configuration, the protection core Yellow/Green is divided in three cores Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Shield Aluminium/polyester tape + Tinned copper wire braid (80%) Total coverage:100% Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
11 | 3G4 | RV-K 0,6/1kV | CWP01 | METERS | 4925 | 5910 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | For all cases no less than 2,5 mm2 (≤14 AWG) will be used. Application For DOL/RDOL starting types, electrical panels supply, etc. Conductor material Copper Isolation XLPE Composition Insulated conductors laid up together. Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Minimun curvature radius 200mm Shield No Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
12 | 6G2,5 | RV-K 0,6/1kV | CWP01 | METERS | 340 | 408 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | For all cases no less than 2,5 mm2(≤14 AWG) will be used. Application For DOL/RDOL starting types, electrical panels supply, etc. Conductor material Copper Isolation XLPE Composition Insulated conductors laid up together. Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Minimun curvature radius 200mm Shield No Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
13 | 4G2,5 | RV-K 0,6/1kV | CWP01 | METERS | 3838 | 4606 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | For all cases no less than 2,5 mm2(≤14 AWG) will be used. Application For DOL/RDOL starting types, electrical panels supply, etc. Conductor material Copper Isolation XLPE Composition Insulated conductors laid up together. Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Minimun curvature radius 200mm Shield No Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
14 | 4G2,5+SH | RC4V-K 0,6/1kV | CWP02 | METERS | 1042 | 1252 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | Application For VFD commanded motor starting types, Thyristor groups fed heaters, etc. Conductor material Copper Isolation XLPE Composition Up to 10mm2: Insulated conductors laid up together. From 16mm2: 3x + 3G configuration, the protection core Yellow/Green is divided in three cores Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Shield Aluminium/polyester tape + Tinned copper wire braid (80%) Total coverage:100% Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
15 | 3G2,5 | RV-K 0,6/1kV | CWP01 | METERS | 4493 | 5392 |  |  |  | 0 | Prosíme doplnit požadované parametry/požadavky na kabel, případně příklad typového označení konkrétního kabelu. | For all cases no less than 2,5 mm2(≤14 AWG) will be used. Application For DOL/RDOL starting types, electrical panels supply, etc. Conductor material Copper Isolation XLPE Composition Insulated conductors laid up together. Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride) Operating voltage 600V/1000V AC Operating temperature Dry ambient: -40ºC, + 90ºC / Wet ambient: -40ºC, + 75ºC Conductor identification To be based on the applicable normative Minimun curvature radius 200mm Shield No Standards IEC 60502-1; Ref. for construction/drawing IEC 60332-1; Flame Retardant | #VALUE!
16 | 7G1,5 | YSLY 300/500V | CWC01 | METERS | 3691 | 4430 |  |  |  | 0 |  | Application Instrumentation Supply, solenoid valves, limit switches and discrete signalling. Conductor material Copper Isolation PVC Composition Insulated conductors laid up together Inner Sheath N/A Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride); grey RAL 7001 Operating voltage 300/500V Operating temperature -40ºC, + 70ºC Conductor identification Black numbered + Yellow/Green Shield No Standards Flame-retardance: VDE 0482-332-1-2/IEC 60332-1-2 | #VALUE!
17 | 5G1,5 | YSLY 300/500V | CWC01 | METERS | 1011 | 1214 |  |  |  | 0 |  | Application Instrumentation Supply, solenoid valves, limit switches and discrete signalling. Conductor material Copper Isolation PVC Composition Insulated conductors laid up together Inner Sheath N/A Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride); grey RAL 7001 Operating voltage 300/500V Operating temperature -40ºC, + 70ºC Conductor identification Black numbered + Yellow/Green Shield No Standards Flame-retardance: VDE 0482-332-1-2/IEC 60332-1-2 | #VALUE!
18 | 4G1,5 | YSLY 300/500V | CWC01 | METERS | 150 | 180 |  |  |  | 0 |  | Application Instrumentation Supply, solenoid valves, limit switches and discrete signalling. Conductor material Copper Isolation PVC Composition Insulated conductors laid up together Inner Sheath N/A Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride); grey RAL 7001 Operating voltage 300/500V Operating temperature -40ºC, + 70ºC Conductor identification Black numbered + Yellow/Green Shield No Standards Flame-retardance: VDE 0482-332-1-2/IEC 60332-1-2 | #VALUE!
19 | 3G1,5 | YSLY 300/500V | CWC01 | METERS | 1011 | 1214 |  |  |  | 0 |  | Application Instrumentation Supply, solenoid valves, limit switches and discrete signalling. Conductor material Copper Isolation PVC Composition Insulated conductors laid up together Inner Sheath N/A Inner Sheath N/A Outher Sheath PVC (Polyvinyl chloride); grey RAL 7001 Operating voltage 300/500V Operating temperature -40ºC, + 70ºC Conductor identification Black numbered + Yellow/Green Shield No Standards Flame-retardance: VDE 0482-332-1-2/IEC 60332-1-2 | #VALUE!
20 | SF/UTP | 6XV1840-2AH10 | CWE01 | METERS | 5464 | 6558 |  |  |  | 0 |  | Application Communication cable used inside the electrical cabinet for all the communication protocols used to communicate main processing unit and all the field equipment. Conductor material Copper Isolation Polyolefin (UL-CSA Standards) Composition Conductors twisted in pairs Outher Sheath PVC Y (UL-CSA Standards) Green Ral 6018 Operating voltage 30V or 300V (600V on request) Operating temperature Dry ambient: -20ºC, + 80ºC Conductor identification White – Yellow – Blue – Orange Shield Aluminum/Plastic Tape and Tinned Copper Braid Coverage ≥ 85% according to EMC 2014/30/EU Conductor section 0,38mm/22AWG Ethernet catergory 5e Standards UL 758 – General marking UL VW-1 – Nonflammable. UL 1581 – Oil and Water resistant | #VALUE!
21 | 6XV1873-2F | 6XV1873-2F FO | CWE03 | METERS | 1030 | 1236 |  |  |  | 0 |  | ApplicationCommunication from the main electrical cabinet for all the communication protocols used to communicate with field equipment when distances are beyond 100m, and Ethernet cables are discarded. Type Multimode optic fibre cable (50/125) Conductor material Optic fibre Isolation Polyolefin (UL-CSA Standards) Composition Insulated conductors laid up together. Outer Sheath Halogen-free compound Operating temperature Dry ambient: -30ºC, +70ºC CPR rating Dca-s2,d2,a1 Standards EN 50173, ISO/IEC 11801, IEC 60794-1 CPR Class: UNE-EN 50575 Flame Propagation: UNE-EN 60332-1 (IEC 60332-1) Halogen-free: UNE-EN 60754-1 (IEC 60754-1) Low fumes emission: UNE-EN 61034 (IEC 61034 | #VALUE!
CELKEM | [9 empty] | 0

## Hoja1 (hidden)
I | Q | 0 | . | 0 | I0.0 | Q0.0 | I | Q | 100 | . | 0 | I100.0 | Q100.0
I | Q | 0 | . | 1 | I0.1 | Q0.1 | I | Q | 100 | . | 1 | I100.1 | Q100.1
I | Q | 0 | . | 2 | I0.2 | Q0.2 | I | Q | 100 | . | 2 | I100.2 | Q100.2
I | Q | 0 | . | 3 | I0.3 | Q0.3 | I | Q | 100 | . | 3 | I100.3 | Q100.3
I | Q | 0 | . | 4 | I0.4 | Q0.4 | I | Q | 100 | . | 4 | I100.4 | Q100.4
I | Q | 0 | . | 5 | I0.5 | Q0.5 | I | Q | 100 | . | 5 | I100.5 | Q100.5
I | Q | 0 | . | 6 | I0.6 | Q0.6 | I | Q | 100 | . | 6 | I100.6 | Q100.6
I | Q | 0 | . | 7 | I0.7 | Q0.7 | I | Q | 100 | . | 7 | I100.7 | Q100.7
I | Q | 1 | . | 0 | I1.0 | Q1.0 | I | Q | 101 | . | 0 | I101.0 | Q101.0
I | Q | 1 | . | 1 | I1.1 | Q1.1 | I | Q | 101 | . | 1 | I101.1 | Q101.1
I | Q | 1 | . | 2 | I1.2 | Q1.2 | I | Q | 101 | . | 2 | I101.2 | Q101.2
I | Q | 1 | . | 3 | I1.3 | Q1.3 | I | Q | 101 | . | 3 | I101.3 | Q101.3
I | Q | 1 | . | 4 | I1.4 | Q1.4 | I | Q | 101 | . | 4 | I101.4 | Q101.4
I | Q | 1 | . | 5 | I1.5 | Q1.5 | I | Q | 101 | . | 5 | I101.5 | Q101.5
I | Q | 1 | . | 6 | I1.6 | Q1.6 | I | Q | 101 | . | 6 | I101.6 | Q101.6
I | Q | 1 | . | 7 | I1.7 | Q1.7 | I | Q | 101 | . | 7 | I101.7 | Q101.7
I | Q | 2 | . | 0 | I2.0 | Q2.0 | I | Q | 102 | . | 0 | I102.0 | Q102.0
I | Q | 2 | . | 1 | I2.1 | Q2.1 | I | Q | 102 | . | 1 | I102.1 | Q102.1
I | Q | 2 | . | 2 | I2.2 | Q2.2 | I | Q | 102 | . | 2 | I102.2 | Q102.2
I | Q | 2 | . | 3 | I2.3 | Q2.3 | I | Q | 102 | . | 3 | I102.3 | Q102.3
I | Q | 2 | . | 4 | I2.4 | Q2.4 | I | Q | 102 | . | 4 | I102.4 | Q102.4
I | Q | 2 | . | 5 | I2.5 | Q2.5 | I | Q | 102 | . | 5 | I102.5 | Q102.5
I | Q | 2 | . | 6 | I2.6 | Q2.6 | I | Q | 102 | . | 6 | I102.6 | Q102.6
I | Q | 2 | . | 7 | I2.7 | Q2.7 | I | Q | 102 | . | 7 | I102.7 | Q102.7
I | Q | 3 | . | 0 | I3.0 | Q3.0 | I | Q | 103 | . | 0 | I103.0 | Q103.0
I | Q | 3 | . | 1 | I3.1 | Q3.1 | I | Q | 103 | . | 1 | I103.1 | Q103.1
I | Q | 3 | . | 2 | I3.2 | Q3.2 | I | Q | 103 | . | 2 | I103.2 | Q103.2
I | Q | 3 | . | 3 | I3.3 | Q3.3 | I | Q | 103 | . | 3 | I103.3 | Q103.3
I | Q | 3 | . | 4 | I3.4 | Q3.4 | I | Q | 103 | . | 4 | I103.4 | Q103.4
I | Q | 3 | . | 5 | I3.5 | Q3.5 | I | Q | 103 | . | 5 | I103.5 | Q103.5
I | Q | 3 | . | 6 | I3.6 | Q3.6 | I | Q | 103 | . | 6 | I103.6 | Q103.6
I | Q | 3 | . | 7 | I3.7 | Q3.7 | I | Q | 103 | . | 7 | I103.7 | Q103.7
I | Q | 4 | . | 0 | I4.0 | Q4.0 | I | Q | 104 | . | 0 | I104.0 | Q104.0
I | Q | 4 | . | 1 | I4.1 | Q4.1 | I | Q | 104 | . | 1 | I104.1 | Q104.1
I | Q | 4 | . | 2 | I4.2 | Q4.2 | I | Q | 104 | . | 2 | I104.2 | Q104.2
I | Q | 4 | . | 3 | I4.3 | Q4.3 | I | Q | 104 | . | 3 | I104.3 | Q104.3
I | Q | 4 | . | 4 | I4.4 | Q4.4 | I | Q | 104 | . | 4 | I104.4 | Q104.4
I | Q | 4 | . | 5 | I4.5 | Q4.5 | I | Q | 104 | . | 5 | I104.5 | Q104.5
I | Q | 4 | . | 6 | I4.6 | Q4.6 | I | Q | 104 | . | 6 | I104.6 | Q104.6
I | Q | 4 | . | 7 | I4.7 | Q4.7 | I | Q | 104 | . | 7 | I104.7 | Q104.7
I | Q | 5 | . | 0 | I5.0 | Q5.0
I | Q | 5 | . | 1 | I5.1 | Q5.1
I | Q | 5 | . | 2 | I5.2 | Q5.2
I | Q | 5 | . | 3 | I5.3 | Q5.3
I | Q | 5 | . | 4 | I5.4 | Q5.4
I | Q | 5 | . | 5 | I5.5 | Q5.5
I | Q | 5 | . | 6 | I5.6 | Q5.6
I | Q | 5 | . | 7 | I5.7 | Q5.7
I | Q | 6 | . | 0 | I6.0 | Q6.0
I | Q | 6 | . | 1 | I6.1 | Q6.1
I | Q | 6 | . | 2 | I6.2 | Q6.2
I | Q | 6 | . | 3 | I6.3 | Q6.3
I | Q | 6 | . | 4 | I6.4 | Q6.4
I | Q | 6 | . | 5 | I6.5 | Q6.5
I | Q | 6 | . | 6 | I6.6 | Q6.6
I | Q | 6 | . | 7 | I6.7 | Q6.7
I | Q | 7 | . | 0 | I7.0 | Q7.0
I | Q | 7 | . | 1 | I7.1 | Q7.1
I | Q | 7 | . | 2 | I7.2 | Q7.2
I | Q | 7 | . | 3 | I7.3 | Q7.3
I | Q | 7 | . | 4 | I7.4 | Q7.4
I | Q | 7 | . | 5 | I7.5 | Q7.5
I | Q | 7 | . | 6 | I7.6 | Q7.6
I | Q | 7 | . | 7 | I7.7 | Q7.7
I | Q | 8 | . | 0 | I8.0 | Q8.0
I | Q | 8 | . | 1 | I8.1 | Q8.1
I | Q | 8 | . | 2 | I8.2 | Q8.2
I | Q | 8 | . | 3 | I8.3 | Q8.3
I | Q | 8 | . | 4 | I8.4 | Q8.4
I | Q | 8 | . | 5 | I8.5 | Q8.5
I | Q | 8 | . | 6 | I8.6 | Q8.6
I | Q | 8 | . | 7 | I8.7 | Q8.7
I | Q | 9 | . | 0 | I9.0 | Q9.0
I | Q | 9 | . | 1 | I9.1 | Q9.1
I | Q | 9 | . | 2 | I9.2 | Q9.2
I | Q | 9 | . | 3 | I9.3 | Q9.3
I | Q | 9 | . | 4 | I9.4 | Q9.4
I | Q | 9 | . | 5 | I9.5 | Q9.5
I | Q | 9 | . | 6 | I9.6 | Q9.6
I | Q | 9 | . | 7 | I9.7 | Q9.7
I | Q | 10 | . | 0 | I10.0 | Q10.0
I | Q | 10 | . | 1 | I10.1 | Q10.1
I | Q | 10 | . | 2 | I10.2 | Q10.2
I | Q | 10 | . | 3 | I10.3 | Q10.3
I | Q | 10 | . | 4 | I10.4 | Q10.4
I | Q | 10 | . | 5 | I10.5 | Q10.5
I | Q | 10 | . | 6 | I10.6 | Q10.6
I | Q | 10 | . | 7 | I10.7 | Q10.7
I | Q | 11 | . | 0 | I11.0 | Q11.0
I | Q | 11 | . | 1 | I11.1 | Q11.1
I | Q | 11 | . | 2 | I11.2 | Q11.2
I | Q | 11 | . | 3 | I11.3 | Q11.3
I | Q | 11 | . | 4 | I11.4 | Q11.4
I | Q | 11 | . | 5 | I11.5 | Q11.5
I | Q | 11 | . | 6 | I11.6 | Q11.6
I | Q | 11 | . | 7 | I11.7 | Q11.7
I | Q | 12 | . | 0 | I12.0 | Q12.0
I | Q | 12 | . | 1 | I12.1 | Q12.1
I | Q | 12 | . | 2 | I12.2 | Q12.2
I | Q | 12 | . | 3 | I12.3 | Q12.3
I | Q | 12 | . | 4 | I12.4 | Q12.4
I | Q | 12 | . | 5 | I12.5 | Q12.5
I | Q | 12 | . | 6 | I12.6 | Q12.6
I | Q | 12 | . | 7 | I12.7 | Q12.7
I | Q | 13 | . | 0 | I13.0 | Q13.0
I | Q | 13 | . | 1 | I13.1 | Q13.1
I | Q | 13 | . | 2 | I13.2 | Q13.2
I | Q | 13 | . | 3 | I13.3 | Q13.3
I | Q | 13 | . | 4 | I13.4 | Q13.4
I | Q | 13 | . | 5 | I13.5 | Q13.5
I | Q | 13 | . | 6 | I13.6 | Q13.6
I | Q | 13 | . | 7 | I13.7 | Q13.7
I | Q | 14 | . | 0 | I14.0 | Q14.0
I | Q | 14 | . | 1 | I14.1 | Q14.1
I | Q | 14 | . | 2 | I14.2 | Q14.2
I | Q | 14 | . | 3 | I14.3 | Q14.3
I | Q | 14 | . | 4 | I14.4 | Q14.4
I | Q | 14 | . | 5 | I14.5 | Q14.5
I | Q | 14 | . | 6 | I14.6 | Q14.6
I | Q | 14 | . | 7 | I14.7 | Q14.7
I | Q | 15 | . | 0 | I15.0 | Q15.0
I | Q | 15 | . | 1 | I15.1 | Q15.1
I | Q | 15 | . | 2 | I15.2 | Q15.2
I | Q | 15 | . | 3 | I15.3 | Q15.3
I | Q | 15 | . | 4 | I15.4 | Q15.4
I | Q | 15 | . | 5 | I15.5 | Q15.5
I | Q | 15 | . | 6 | I15.6 | Q15.6
I | Q | 15 | . | 7 | I15.7 | Q15.7

## Seed (hidden)
Signal nature | Protocol type
Wired | Wired | N/A
Comms | Comms | PROFINET
| Comms | PROFIBUS
| Comms | MODBUS RTU
| Comms | MODBUS TCP