## Hárok1
Reconstruction of Membrane Walls and Replacement of Superheaters of K1, K2 Boilers in ZEVO Plant Bratislava
Pos. | Content | Scope | Material | Drawing | Unit | Quantity | Unit price in EUR without VAT | Total price EUR without VAT
| Replacement of front membrane wall in incineration chamber approx. 25 m2 | K1, K2 |  | 104, 105
1 | Technical processing (Construction processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
2 | Material and production of part of membrane wall approx.. 25 m2 from pipes Ø 60.3 x 5, t=78 |  | St 35.8I |  | kpl | 2
3 | Cladding of layer NiCr625 ≥ 2 mm (workshop made) on part of membrane wall approx. 15 m2 |  | NiCr625 |  | kpl | 2
4 | removal of existing membrane wall and respective elements |  |  |  | kpl | 2
5 | General preparation of welds |  |  |  | kpl | 2
6 | Installation of new part of membrane wall and installation of respective elements |  |  |  | kpl | 2
| Replacement of a part of right membrane wall in the incineration chamber approx. 38 m2 | K1, K2 |  | 103, 105
7 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
8 | Material and production of part of membrane wall approx. 38 m2 from pipes Ø 60.3 x 5, t=78 |  | St 35.8I |  | kpl | 2
9 | Cladding of layer NiCr625 ≥ 2 mm (workshop made) on part of membrane wall approx. 25 m2 |  | NiCr625 |  | kpl | 2
10 | removal of existing membrane wall and respective elements |  |  |  | kpl | 2
11 | General preparation of welds |  |  |  | kpl | 2
12 | Installation of new part membrane wall and installation of respective elements |  |  |  | kpl | 2
| Replacement of part of left membrane wall in the incineration chamber approx. 38 m2 | K1, K2 |  | 103, 105
13 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
14 | Material and production of part of membrane wall approx. 38 m2 from pipes Ø 60,3 x 5, t=78 |  | St 35.8I |  | kpl | 2
15 | Cladding of layer NiCr625 ≥ 2 mm (workshop made) on parts of membrane wall approx. 25 m2 |  | NiCr625 |  | kpl | 2
16 | removal of existing membrane wall and respective elements |  |  |  | kpl | 2
17 | General preparation of welds |  |  |  | kpl | 2
18 | Installation of new part membrane wall and installation of respective elements |  |  |  | kpl | 2
| Treatment of joints (welds) between existing and new parts of membrane walls | K1, K2 |  | 103, 104
19 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
20 | 1st layer circumferential welding of contact joints of membrane walls |  | according WPS |  | kpl | 2
21 | 2nd layer NiCr625 cladding from interior side of membrane walls |  | NiCr625 |  | kpl | 2
| Cladding of layer NiCr625 in incineration chamber of boiler on rear wall (on-site) approx. 23 m | K1, K2 |  | 101, 105
22 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
23 | Surface finish of pipes with anti-corrosion coating (after sand-blasting) |  |  |  | kpl | 2
24 | Cladding of NiCr625 layer (by automatic and manual welding) |  |  |  | kpl | 2
| Cladding of NiCr625 layer in incineration chamber on front wall - on vertical pipes of secondary air outlet (on-site) | K1, K2 |  | 101, 105
25 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
26 | Surface finish of pipes with anti-corrosion coating (after sand-blasting) |  |  |  | kpl | 2
27 | Cladding of NiCr625 layer (by automatic and manual welding) |  | NiCr625 |  | kpl | 2
| Local repairs of NiCr625 cladding in incineration chamber of boiler also in second and third draught of boiler | K1, K2 |  | 101
28 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
29 | Surface finish of pipes with anti-corrosion coating (after sand-blasting) |  |  |  | m2
30 | Local repairs of NiCr625 cladding by manual welding |  | NiCr625 |  | m2
| Cladding of NiCr625 layer in boiler above infeed table (approx. 4.5 m2) | K1, K2 |  | 101, 105
31 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
32 | Surface finish of pipes with anti-corrosion coating (after sand-blasting) |  |  |  | kpl | 2
33 | Cladding of NiCr625 layer (by automatic and manual welding) |  | NiCr625 |  | kpl | 2
| Production, installation and removal of scaffolding supporting consoles of 2nd and 3rd draught of boiler | K1, K2
34 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
35 | Material and production |  | construc. steel |  | kpl | 2
36 | Installation |  |  |  | pcs | 16
37 | Removal |  |  |  | pcs | 16
| Replacement of steam superheater No. I/1 | K1, K2 |  | 101, 106
38 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
39 | Straight seamless pipes Ø 44.5 x 5 |  | 15Mo3 |  | pcs | 80
40 | Bent seamless pipes Ø 44.5 x 5 with elbow 180˚ |  | 15Mo3 |  | pcs | 80
41 | Suspension clamp Ø 12 x 272 with thread |  | X10CrAI7 |  | pcs | 72
42 | Suspension clamp Ø 12 x 322 with thread |  | X10CrAI7 |  | pcs | 8
43 | Removal of existing pipes |  |  |  | pcs | 160
44 | Installation of new pipes + General preparation of welds |  |  |  | pcs | 160
| Replacement of steam superheater No. II | K1 |  | 101a, 106
45 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 1
46 | Straight seamless pipes Ø 44.5 x 5 |  | 15Mo3 |  | pcs | 4
47 | Suspension clamp Ø 12 x 272 with thread |  | X10CrAI7 |  | pcs | 90
48 | Suspension clamp Ø 12 x 320 with thread |  | X10CrAI7 |  | pcs | 6
49 | Suspension clamp Ø 16 x 295 with thread |  | X10CrAI7 |  | pcs | 6
50 | Removal of existing pipes |  |  |  | pcs | 136
51 | Installation of new pipes + General preparation of welds |  |  |  | pcs | 136
| Replacement of steam superheater No. II | K2 |  | 101b, 107
52 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 1
53 | Straight seamless pipes Ø 44.5 x 5 |  | 15Mo3 |  | pcs | 68
54 | Bent seamless pipes Ø 44.5 x 5 with elbow 180˚ |  | 15Mo3 |  | pcs | 204
55 | Suspension clamp Ø 12 x 272 with thread |  | X10CrAI7 |  | pcs | 180
56 | Suspension clamp Ø 12 x 320 with thread |  | X10CrAI7 |  | pcs | 12
57 | Suspension clamp Ø 16 x 295 with thread |  | X10CrAI7 |  | pcs | 12
58 | Removal of existing pipes |  |  |  | pcs | 272
59 | Installation of new pipes + General preparation of welds |  |  |  | pcs | 272
| Replacement of steam superheater No. I/2 | K1 |  | 101a, 106
60 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 1
61 | Straight seamless pipes Ø 44.5 x 5 |  | 15Mo3 |  | pcs | 68
62 | Bent seamless pipes Ø 44.5 x 5 with elbow 180˚ |  | 15Mo3 |  | pcs | 238
63 | Suspension clamp Ø 12 x 272 with thread |  | X10CrAI7 |  | pcs | 210
64 | Suspension clamp Ø 12 x 320 with thread |  | X10CrAI7 |  | pcs | 14
65 | Suspension clamp Ø 16 x 295 with thread |  | X10CrAI7 |  | pcs | 14
66 | Removal of existing pipes |  |  |  | pcs | 306
67 | Installation of new pipes + General preparation of welds |  |  |  | pcs | 306
| Replacement of steam superheater No. I/2 | K2 |  | 101b, 107
68 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 1
69 | Straight seamless pipes Ø 44.5 x 5 |  | 15Mo3 + 1 mm NiCr625 |  | pcs | 34
70 | Bent seamless pipes Ø 44.5 x 5 with elbow 180˚ |  | 15Mo3 + 1 mm NiCr625 |  | pcs | 136
71 | Straight seamless pipes Ø 44.5 x 5 |  | 15Mo3 |  | pcs | 34
72 | Bent seamless pipes Ø 44.5 x 5 with elbow 180˚ |  | 15Mo3 |  | pcs | 102
73 | Suspension clamp Ø 12 x 272 with thread |  | X10CrAI7 |  | pcs | 210
74 | Suspension clamp Ø 12 x 320 with thread |  | X10CrAI7 |  | pcs | 14
75 | Suspension clamp Ø 16 x 295 with thread |  | X10CrAI7 |  | pcs | 14
76 | Removal of existing pipes |  |  |  | pcs | 306
77 | Installation of new pipes + General preparation of welds |  |  |  | pcs | 306
| Repair of Economizer (ECO) | K1, K2 |  | 101, 106, 107
78 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
79 | Bent seamless pipes (coils) Ø 33.7 x 4 with elbow 180˚ |  | St 35.8I |  | pcs | 50
80 | Suspension clamp Ø 10 x 236 |  | X10CrAI7 |  | pcs | 50
81 | Removal of existing pipes |  |  |  | pcs | 50
82 | Installation of new pipes + General preparation of welds |  |  |  | pcs | 50
| Tests | K1, K2
83 | X-ray tests 10% RTG |  |  |  | kpl | 2
84 | Measurement of wall thickness of pipes and thickness of NiCr625 cladding |  |  |  | kpl | 2
85 | Tests of Fe content |  |  |  | kpl | 2
| Optimization of incineration process in the incineration chamber after change of scope of refractory lining | K1, K2
86 | Technical processing (constructional processing, proposal of tests, welding plans - WPS, quality control proposal) |  |  |  | kpl | 2
87 | Implementation |  |  |  | kpl | 2
88 | Documentation of reconstruction performed | K1, K2 |  |  | kpl | 2
89 | Plan of quality, plan of checks and tests, accompanying documentation | K1, K2 |  |  | kpl | 2
90 | Documentation of real implementation | K1, K2 |  |  | kpl | 2
91 | Setup, tests, commissioning/start-up | K1, K2 |  |  | kpl | 2
92 | Engineering (project leadership, management and coordination of the Work) | K1, K2 |  |  | kpl | 2
93 | Travelling costs (employees) | K1, K2 |  |  | kpl | 2
94 | Filler welding materials | K1, K2 |  |  | kpl | 2
95 | Grinding and means of separation | K1, K2 |  |  | kpl | 2
96 | Personal protection means | K1, K2 |  |  | kpl | 2
97 | Costs of tools | K1, K2 |  |  | kpl | 2
98 | Costs of transport of tools | K1, K2 |  |  | kpl | 2
99 | Total costs of transport of membrane walls and superheaters | K1, K2 |  |  | kpl | 2
∑ Total price (excluding VAT) | [7 empty] | 0